Engineering Specification

Model F1FR Quick Response

Sidewall Sprinklers

Sprinklers shall be standard coverage, quick response [horizontal sidewall] [recessed horizontal sidewall] [vertical sidewall] sprinklers that are [cULus Listed][FM Approved [NYC MEA Approved – 258-93-E] for light hazard occupancies.  Sprinkler frame and deflector shall be of bronze frame construction having a [½”][ ¾”] NPT thread.  Water seal assembly shall consist of a Teflon-coated Belleville spring washer and top-loaded extruded cup with 3 mm glass bulb containing no plastic parts. Sprinkler temperature rating shall be [135 (F (57 (C)] [155 (F (68 (C)] [175 (F (79 (C)] [200(F (93(C)] [286 (F (141 (C)].  Sprinklers shall have a nominal K-factor of 5.6 (81.0) – standard orifice.  Sidewall Sprinklers shall have a rated working pressure of 175 psi (12.1 bar). [The vertical sidewall shall be installed in the [upright] [pendent] position. Standard finish: [Bronze] [Chrome-plated] [Special finish– specify].  Sprinklers shall be Reliable Model F1FR [horizontal sidewall – SIN R3635] [vertical sidewall – SIN R3685], Bulletin 136.

## Escutcheon Options

### Model F2 escutcheon (horizontal sidewall only)

Recessed escutcheon assembly shall be a steel, two-piece, friction-fit escutcheon with 1/2” adjustment.   Standard finish shall be [brass][bright chrome] [white painted].